## Health Faults
Format: Microsoft.Health.FaultType.<Type>.<Fault>
Type | Fault | Health Urgency | Severity | Title | Description | Action | Action (Active)
PhysicalDisk | LostCommunication | Unhealthy | Critical | The drive is missing. | Windows cannot communicate with the drive. It may be loose or disconnected, its connector may have failed, or the drive itself may have failed. Windows automatically retires drives after 15 minutes of lost communication. | Check that the drive is working and properly connected. If communication resumes, Windows will automatically start using the drive again. If the drive has failed, replace it.
PhysicalDisk | FailedMedia | Unhealthy | Critical | The drive failed. | The physical drive permanently failed. | Replace the drive.
PhysicalDisk | SblFailedMedia | Unhealthy | Critical | The drive failed. | The physical drive permanently failed. | Replace the drive.
PhysicalDisk | PredictiveFailure | Unhealthy | Critical | The drive reported it may fail soon. | The drive reported to Windows that it may fail soon. It reported this using SMART (Self-Monitoring, Analysis and Reporting Technology) or another similar technology. The manufacturer may have tools that can provide more detail. | Replace the drive.
PhysicalDisk | UnrecognizedMetadata | Unhealthy | Critical | The drive has unrecognized metadata. | The drive has unrecognized metadata, which usually means that the drive has data from a previous storage pool on it. | This disk may contain data from an unknown storage pool. First make sure there is no useful data on this disk, then reset the disk.
PhysicalDisk | UnsupportedHardware | Unhealthy | Critical | The drive is unsupported hardware. | Your solution vendor doesn't allow adding this model of drive to the storage pool. | Replace the drive with supported hardware.
PhysicalDisk | UnsupportedFirmware | Unhealthy | Critical | The drive has unsupported firmware. | Your solution vendor doesn't allow adding drives with this firmware version to the storage pool. | Update the firmware on the drive to the target version. | Updating the firmware on the drive to the target version.
PhysicalDisk | Unresponsive | Unhealthy | Critical | The drive isn't responding. | The drive has repeatedly taken many seconds to respond to commands within the last hour. | If this keeps happening, consider replacing the drive by removing it and inserting its replacement into the same location.
PhysicalDisk | SblUnresponsive | Unhealthy | Critical | The drive isn't responding. | The drive has repeatedly taken many seconds to respond to commands within the last hour. | If this keeps happening, consider replacing the drive by removing it and inserting its replacement into the same location.
PhysicalDisk | FailedFirmwareUpdate | Unhealthy | Critical | Couldn't update the drive firmware. | Windows couldn't update the firmware on this drive. The provided firmware file might not work, or the drive might not support Windows managing firmware updates. | "Try using a different firmware binary." or "Manually attempt to update the physical disk's firmware." or "Replace the physical disk with another disk that has the desired firmware."
PhysicalDisk | FailureBadBlock | Warning | Minor | The drive might be failing. | The drive reported {0} bad blocks during writes in the last {2} days {3} hours. An occasional bad block is normal, but too many could mean that the drive is malfunctioning, damaged, or beginning to fail. | If this keeps happening or you observe decreased performance, consider replacing the drive.
PhysicalDisk | FailureBadBlockRead | Warning | Minor | The drive might be failing. | The drive reported {0} bad blocks during reads in the last {2} days {3} hours. An occasional bad block is normal, but too many could mean that the drive is malfunctioning, damaged, or beginning to fail. | If this keeps happening or you observe decreased performance, consider replacing the drive.
PhysicalDisk | FailureIoRetry | Warning | Minor | The drive might be failing. | The drive needed multiple tries to read or write {0} times in the last {2} days {3} hours. If this keeps happening, it could mean that the drive is malfunctioning, damaged, or beginning to fail. | If this keeps happening or you observe decreased performance, consider replacing the drive.
PhysicalDisk | FailureIoFailure | Warning | Minor | The drive might be failing. | The drive failed to read or write {0} times in the last {2} days {3} hours. If this keeps happening, it could mean that the drive is malfunctioning, damaged, or beginning to fail. | If this keeps happening or you observe decreased performance, consider replacing the drive.
PhysicalDisk | FailureSmart | Healthy | Degraded/Warning | The drive reported potential problems. | The drive reported the following potential problems to Windows using SMART (Self-Monitoring, Analysis and Reporting Technology): {0} | If this keeps happening or you observe decreased performance, consider replacing the drive.
PhysicalDisk | FailureHighWear | Warning | Minor | The drive is wearing out. | The drive has reached {0}% of its rated write endurance. The drive may become read-only, meaning it cannot perform any more writes, when it reaches 100% of its rated endurance. Check the data sheet or ask the manufacturer for more details about endurance rating and end-of-life behavior. | If this keeps happening or you observe decreased performance, consider replacing the drive.
PhysicalDisk | FailureReadOnly | Unhealthy | Critical | The drive is worn out. | The drive reached 100% of its rated write endurance and is now read-only, meaning it cannot perform any more writes. Solid-state drives wear out after a certain number of writes, which varies depending on the endurance rating of the drive. For details, check the drive specifications or ask the manufacturer about endurance rating and end-of-life behavior. | Replace the drive.
PhysicalDisk | HighLatency | Warning | Minor | The drive is performing slowly. | The drive has high average latency. In the last {0} minutes, it took an average of {1}ms to read or write, exceeding your configured {2}ms warning threshold. If this keeps happening, it may indicate that the drive is malfunctioning, damaged, or beginning to fail. | Monitor the drive's performance and consider replacing the drive.
PhysicalDisk | HighLatency.SlowestIO | Warning | Minor | The drive is performing slowly. | The drive has high peak latency. In the last {0} minutes, {1}% of reads or writes took longer than {2}ms, exceeding your configured {3}% warning threshold. If this keeps happening, it may indicate that the drive is malfunctioning, damaged, or beginning to fail. | Monitor the drive's performance and consider replacing the drive.
PhysicalDisk | HighLatency.AverageIO | Warning | Minor | The drive is performing slowly. | The drive has high average latency. In the last {0} minutes, it took an average of {1}ms to read or write, exceeding your configured {2}ms warning threshold. If this keeps happening, it may indicate that the drive is malfunctioning, damaged, or beginning to fail. | Monitor the drive's performance and consider replacing the drive.
PhysicalDisk | HighLatency.Outlier.AverageIO | Warning | Minor | The drive is performing slowly. | The drive has high average latency. In the last {0} minutes, it took an average of {1}ms to read or write, compared to {2}ms for similar drives in the cluster with similar activity. If this keeps happening, it may indicate that the drive is malfunctioning, damaged, or beginning to fail. | Monitor the drive's performance and consider replacing the drive.
PhysicalDisk | HighLatency.Outlier.SlowestIO | Warning | Minor | The drive is performing slowly. | The drive has high peak latency. In the last {0} minutes, {1}% of reads or writes took longer than {3}ms, compared to {2}% for similar drives in the cluster with similar activity. If this keeps happening, it may indicate that the drive is malfunctioning, damaged, or beginning to fail. | Monitor the drive's performance and consider replacing the drive.
PhysicalDisk | HighErrorCount.AverageIO | Warning | Minor | The drive is having a high number of errors. | The drive has high number of errors. In the last {0} minutes, it had {1} errors to read or write, exceeding your configured {2} warning threshold. If this keeps happening, it may indicate that the drive is malfunctioning, damaged, or beginning to fail. | Monitor the drive's performance and consider replacing the drive.
PhysicalDisk | HighErrorCount.Outlier.AverageIO | Warning | Minor | The drive is having a high number of errors. | The drive has high number of errors. In the last {0} minutes, it had {1} errors to read or write, compared to {2} for similar drives in the cluster with similar activity. If this keeps happening, it may indicate that the drive is malfunctioning, damaged, or beginning to fail. | Monitor the drive's performance and consider replacing the drive.
PhysicalDisk | CacheReadOnly | Warning | Minor | The cache drive isn't in use. | The cache drive failed some reads or writes, so to protect your data we've moved it onto capacity drives. | Replace the drive or try to clear and reset it.
PhysicalDisk | CacheReadOnly.Draining | Warning | Minor | We're moving data off a failing cache drive. | The cache drive failed some reads or writes. To protect your data, we've stopped writing to the cache drive and we're trying to move its data onto capacity drives. | Hang on while we move the data. | Moving data off a failing cache drive.
PhysicalDisk | CacheReadOnly.FailedDrain | Unhealthy | Critical | Can't read some data on the cache drive. | Some data on the cache drive can't be read, preventing us from moving it onto capacity drives. | Replace the drive.
PhysicalDisk | SedEncKey.RotationFailure | Unhealthy | Critical | Failed to rotate SED encryption key. | The attempt to rotate SED encryption key to the new default failed. | Check that the drive is working and properly connected. If the drive has failed, replace it. Restart SED encryption key rotation once the drive is healthy.
PhysicalDisk | SedEncKey.NotDefault | Warning | Minor | Using SED encryption key other than the default. | The physical disk has a SED encryption key, however it does not match the current default key. | Initiate SED encryption key rotation.
PhysicalDisk | SedEncKey.NotDefined | Warning | Minor | SED encryption key not defined. | There is no defined default SED encryption key for the drive. | Set a default SED encryption key
PhysicalDisk | DriveArriveFailure | Unhealthy | Critical | Storage Space Drive Arrive Failure. | Physical Disk is failing queries. | Please validate network reliability. If the issue persists, consider replacing the device.
StorageEnclosure | LostCommunication | Unhealthy | Critical | Communication with the enclosure has been lost. | Windows cannot communicate with the storage enclosure '{0}'. It may be disconnected or it may have failed. | Start or replace the storage enclosure.
StorageEnclosure | FanError | Warning | Minor | The fan has failed. | The fan at position '{0}' of the storage enclosure at location '{1}' has failed. | Replace the fan in the storage enclosure.
StorageEnclosure | CurrentSensorError | Warning | Minor | The current sensor has failed. | The current sensor at position '{0}' of the storage enclosure at location '{1}' has failed. | Replace a current sensor in the storage enclosure.
StorageEnclosure | IoControllerError | Warning | Minor | The IO controller has failed. | The IO controller at position '{0}' of the storage enclosure at location '{1}' has failed. | Replace an IO controller in the storage enclosure.
StorageEnclosure | TemperatureSensorError | Warning | Minor | The temperature sensor has failed. | The temperature sensor at position '{0}' of the storage enclosure at location '{1}' has failed. | Replace a temperature sensor in the storage enclosure.
StorageEnclosure | VoltageSensorError | Warning | Minor | The voltage sensor has failed. | The voltage sensor at position '{0}' of the storage enclosure at location '{1}' has failed. | Replace a voltage sensor in the storage enclosure.
StorageEnclosure | EmptySlotsError | Healthy | Minor | The enclosure has empty drive slots. | Slots '{0}' of the storage enclosure at location '{1}' are empty or have failed drives. | Add or replace disks in the storage enclosure.
StorageScaleUnit | SedEncKey.RotationTimeout | Warning | Minor | SED encryption key rotation timeout. | Failed to complete SED encryption key rotation on the server '{0}' before timeout. | Ensure the server is reachable and that all physical disks are healthy
Volume | Capacity | Warning | Minor | The volume is almost full. | The volume '{0}' is running low on available storage capacity. | Resize the volume, delete unwanted files, or move files to other volumes
Volume | HighLatency | Warning | Minor | The volume has high latency. | The volume has high average latency. In the last {0} minutes, it took an average of {1}ms to read or write, exceeding your configured {2}ms warning threshold. | IDS_VOLUME_HIGH_LATENCY_ACTION - 415
Volume | FileSystem.Corruption.Correctable | Warning | Minor | Correctable file system corruption detected. | The file system detected a checksum error and was able to correct it. The file(s) or folder(s) impacted are {0} | Initiate Data Integrity scan from task scheduler, storage might be going bad. If there is an update or maintenance operation going on, stop it immediately. You may need to restore from the backup.
Volume | FileSystem.Corruption.Uncorrectable | Unhealthy | Critical | Uncorrectable file system corruption detected. | The file system detected a checksum error and was not able to correct it. The file(s) or folder(s) impacted are {0} | Initiate Data Integrity scan from task scheduler, storage might be going bad. If there is an update or maintenance operation going on, stop it immediately. You may need to restore from the backup.
Volume | FileSystem.Corruption.Uncorrectable.DataRemoved | Unhealthy | Critical | Uncorrectable file system corruption detected with data removed. | The file system detected a corruption on a file or folder. The file or folder has been removed from the file system namespace. The file(s) or folder(s) impacted are {0} | Initiate Data Integrity scan from task scheduler, storage might be going bad. If there is an update or maintenance operation going on, stop it immediately. You may need to restore from the backup.
Volume | FileSystem.Corruption.Uncorrectable.DataRemovalFailure | Unhealthy | Critical | Uncorrectable file system corruption detected with data removed failure. | The file system detected a corruption on a file or folder. The file system may have failed to remove it from the file system namespace. The file(s) or folder(s) impacted are {0} | Initiate Data Integrity scan from task scheduler, storage might be going bad. If there is an update or maintenance operation going on, stop it immediately. You may need to restore from the backup.
VirtualDisks | NeedsRepair | Healthy | Degraded/Warning | The volume needs to sync. | All data on this volume is safe and accessible, but we need to sync it with data from other servers in the cluster. This is normal after a server restarts or a drive fails. | Hang on while we sync the storage. Don't remove any drives or restart any servers in the cluster until we confirm that the sync is complete. | Hang on while we sync the storage.
VirtualDisks | Detached | Unhealthy | Critical | The volume is offline. | The volume is inaccessible, which can happen when an administrator takes it offline, or when too many drives or servers fail or become disconnected. | Reconnect any missing drives and bring up any servers that are down. Don't remove any drives or restart any servers in the cluster until we confirm that the sync is complete. After the storage finishes syncing, replace any failed drives and restore any lost data from backup.
VirtualDisks | NoRedundancy | Unhealthy | Critical | No Redunancy Failure | All copies of data are unavailable for a region of virtual disk. Workload may be interrupted and IO failures may be observed. | If a maintenance operation is ongoing, please suspend it and restore access to all storage until the storage stabilizes.
VirtualDisks | LastCopy | Healthy | Degraded/Warning | Last Copy Failure | Parts of the virtual disk have one available copy of data. Failure of a disk, enclosure, node or rack will cause the volume to become unavailable and could lead to data loss. To see a list of physical disks that holding the last copy of data, please use Get-PhysicalDisk -NoRedundancy command. | Bring online nodes and disks as soon as possible to bring back redundancy.
StoragePool | InsufficientReserveCapacity | Warning | Minor | Storage pool needs additional capacity to repair automatically. | Storage pool needs additional capacity to repair automatically. The storage pool doesn't have enough available capacity to repair volumes after drive failures without waiting for a drive replacement. | Add additional capacity to the storage pool or free up capacity. We recommend leaving unallocated the equivalent of one capacity drive per server, up to four drives. For details, see [Reserve capacity](https://go.microsoft.com/fwlink/?linkid=2257735).
StoragePool | TransactionAndCleanupFailure | Unhealthy | Critical | Storage Space Transaction and Cleanup Failure. | Storage Pool is unable to write to a quorum of metadata devices. Workload may be interrupted and IO failures may be observed. | If a maintenance operation is ongoing, please suspend it and restore access to all storage until the storage stabilizes.
StoragePool | PoolCapacityThresholdExceeded | Warning | Minor | Storage pool threshold alert for thin provisioning. | The storage pool is running out of capacity. The configurable threshold is set to {0}% currently. | Add additional capacity to the storage pool or free up capacity.
Server | Down | Unhealthy | Critical | The server is down. | Other servers in the cluster cannot reach server '{0}'. This could be because the cluster service isn't running on the server, it lost power or is turned off, or it lost network connectivity. | Check that the server is turned on and connected to the network. Then try connecting to the server and start the Cluster service if it isn't running - either by using the Services tool or the Get-Service and Start-Service cmdlets in PowerShell.
Server | Quarantined | Unhealthy | Critical | The server is quarantined by the cluster. | The server '{0}' is quarantined by the cluster because it left the cluster three times within an hour without giving a notification to the cluster. For the next two hours, the server cannot rejoin the cluster. This action prevents its transient failures from negatively impacting other servers or the overall cluster. Virtual machines hosted by the server are moved without downtime to other servers. | Try troubleshooting the server and potential network issues.
Server | Temperature | Warning | Minor | The server temperature sensor has raised a warning. | The temperature sensor on the motherboard of server '{0}' has raised a warning. | Check the server temperature.
Server | Storage.Degraded | Warning | Minor | The server needs to sync its storage. | The server has storage that isn't complete or up-to-date, so we need to sync it with data from other servers in the cluster. This is normal after a server restarts or a drive fails. | Hang on while we sync the storage. Don't remove any drives or restart any servers in the cluster until we confirm that the sync is complete.
StorageSubsystem | RDMA.Alert | Healthy | Degraded/Warning | The cluster | The cluster detected network connectivity issues that prevent Storage Spaces Direct from working properly. | Verify that your network is properly configured and working. If you are using RDMA Over Converged Ethernet (RoCE), verify that Data Center Bridging (DCB), Enhanced Transmission Service (ETS), and Priority Flow Control (PFC) are configured correctly and consistently on every cluster node and physical switch. If you don't know how to do this, ask your vendor or someone you trust to help you.
StorageSubsystem | RDMA.Disabled | Warning | Minor | The cluster | The cluster detected network connectivity issues that prevent Storage Spaces Direct from working properly. To ensure consistent performance and data safety, Storage Spaces Direct has stopped using remote direct memory access (RDMA) even if RDMA-capable hardware is present and enabled. Storage traffic will continue to flow but with diminished performance using TCP/IP. | Verify that your network is properly configured and working, and then turn RDMA back on. If you are using RDMA Over Converged Ethernet (RoCE), verify that Data Center Bridging (DCB), Enhanced Transmission Service (ETS), and Priority Flow Control (PFC) are configured correctly and consistently on every cluster node and physical switch. If you don't know how to do this, ask your vendor or someone you trust to help you. To continue with RDMA turned off, you can dismiss this alert.
ClusterQuorumWitness | Error | Warning | Minor | The cluster quorum witness resource is offline. | The cluster quorum witness resource is offline. | Check the witness resource, and restart as needed. Start or replace failed servers.
Cluster | ValidationReport.Failed | Unhealthy | Critical | The cluster | Cluster Validation has found failures in {0} categories of tests. Cluster Configuration: {1}, Hyper-V Configuration: {2}, Inventory: {3}, Network: {4}, Storage: {5}, Storage Spaces Direct: {6}, System Configuration: {7}. See cluster validation report here: '{8}'. | Cluster Validation has found problems.
Cluster | ValidationReportDcb.Failed | Unhealthy | Critical | The cluster | Validate-DCB has found problems. | Validate-DCB has found {0} networking errors. See DCB validation report here: '{1}'.
NetworkInterface | Missing | Unhealthy | Critical | The network interface is missing. | The server '{0}' is not connected to cluster network '{1}'. | Connect the server to the missing cluster network.
NetworkAdapter | Disconnected | Unhealthy | Critical | The network adapter is disconnected. | The network adapter '{0}' is disconnected. The cable may be loose or disconnected, the cable may have failed, or the network adapter itself may have failed. | Check that the network cable is working and properly connected.
NetworkAdapter | Disabled | Warning | Minor | The network adapter is disabled. | The network adapter '{0}' is disabled, so Windows isn't using it. | If you want to use this network adapter for communication, enable it. Otherwise, feel free to ignore this.
NetworkAdapter | Hardware | Unhealthy | Critical | The network adapter has failed. | The network adapter '{0}' has experienced a hardware failure. | Replace the network adapter.
StoreQos | InsufficientThroughput | Unhealthy | Critical | <Object Specific> | Storage throughput is insufficient to satisfy reserves. | Move heavily accessed files to volumes with spare throughput. Reconfigure Storage QoS policies.
StoreQos | LostCommunication | Unhealthy | Critical | <Object Specific> | The Storage QoS policy manager has lost communication with the volume. | Please reboot nodes {0}
StoreQos | MisconfiguredFlow | Unhealthy | Critical | <Object Specific> | One or more storage consumers (usually Virtual Machines) are using a non-existent policy with id {0}. Consumer details:\r\n\r\nFlow ID: {1}\r\nInitiator ID: {2}\r\nInitiator Name: {3}\r\nInitiator Node: {4}\r\nFile Path: {5} | Reconfigure the storage consumers (usually Virtual Machines) to use a valid policy. Recreate any missing Storage QoS policies.
FaultDomain | FailedMaintenanceMode | Warning | Minor | The firmware rollout is waiting. | The firmware rollout cannot proceed until all servers are up and all volumes have full resiliency. Windows will try again automatically later. | Verify all storage spaces are healthy, and that no fault domain is currently in maintenance mode.
FaultDomain | TooManyFailedUpdated | Warning | Minor | The firmware rollout is cancelled. | The firmware rollout has been cancelled because too many drives failed to apply the update. The provided firmware file might not be valid, or this model of drive might not supported Windows-native firmware updates.
FaultDomain | FirmwareVerifyVersionFailed | Unhealthy | Critical | The firmware rollout stopped. | After applying an update to drive firmware, Windows couldn't verify that the update was successful. The firmware rollout has been cancelled for all subsequent drives as a precaution.
Node | CPUOverloaded | Unhealthy | Critical | The server is low on CPU resources. | The server's CPU utilization is consistently over {0}%. | Move virtual machines to other servers with lower CPU usage, or consider adding additional compute capacity to the cluster (usually by adding servers.
Node | VCPUToLCPU | Unhealthy | Critical | The server has too many virtual processors. | The ratio of virtual processors to logical processors (threads) on this server has exceeded your configured threshold of {0}. | Move virtual machines to another server with lower CPU usage or consider adding additional compute capacity to the cluster.
Node | HighRootPartitionMemoryUsage | Unhealthy | Critical | The host OS is using too much memory. | Windows Server is consuming more than {0} of physical memory, which exceeds your configured threshold. | Check for processes or apps consuming too much memory, move virtual machines to other servers, or add memory to the servers.
Node | TooHighCpuReservation | Unhealthy | Critical | The CPU reservations for VMs are too high. | The combined CPU reservation of virtual machines on this server exceeds your configured threshold of {0}. | Consider moving virtual machines or reducing their CPU reservations.
Node | TooHighMemoryUseAfterReclamation | Unhealthy | Critical | The memory assigned to VMs is too high. | The combined memory assignment of virtual machines on this server exceeds the your configured threshold of {0}. | Consider moving virtual machines or reducing their assigned memory.
Node | SustainedHighCpuUsage | Unhealthy | Critical | The server has high CPU usage. | The server has CPU usage consistently exceeding {0}. | Move virtual machines to another server with lower CPU usage or consider adding more compute capacity.
Cluster | TooHighCpuReservation | Unhealthy | Critical | The CPU reservations for VMs are too high. | The combined CPU reservation of virtual machines on this server exceeds your configured threshold of {0}. | Consider moving virtual machines or reducing their CPU reservations.
Cluster | TooHighMemoryuseAfterReclamation | Unhealthy | Critical | The memory assigned to VMs is too high. | The combined memory assignment of virtual machines on this server exceeds the your configured threshold of {0}. | Consider moving virtual machines or reducing their assigned memory.
Cluster | SustainedHighCpuUsage | Unhealthy | Critical | The server has high CPU usage. | The server has CPU usage consistently exceeding {0}. | Move virtual machines to another server with lower CPU usage or consider adding more compute capacity.
Vm | BadHealthState | Unhealthy | Critical | The virtual machine is unhealthy. | The virtual machine health state isn't OK. | Troubleshoot the virtual machine.
Vm | BadOperationalStatus | Unhealthy | Critical | The virtual machine is unhealthy. | The virtual machine operational status isn't OK. | Troubleshoot the virtual machine.
Vm | GuestUnhealthy | Unhealthy | Critical | The OS in the VM is unhealthy. | The guest operating system in the virtual machine is reporting an unhealthy state. | Troubleshoot the virtual machine.
Vm | ConfigIsOffline | Unhealthy | Critical | The VM configuration resource is offline. | The virtual machine configuration resource is offline, meaning the virtual machine cannot be administered. | Bring the virtual machine configuration online.
Vm | NotRespondingToControlCodes | Unhealthy | Critical | The VM isn't responding. | The virtual machine isn't responding to cluster control codes. | Check the state of the virtual machine cluster resource.
Vm | IsNearMemoryLimit | Unhealthy | Critical | The VM is low on memory. | The virtual machine needs more than {0} of its configured maximum memory. | Check for processes or apps consuming too much memory or consider increasing its maximum memory.
Vhd | IsNearlyFull | Healthy | Degraded/Warning | The virtual hard disk is full. | The virtual hard disk has reached its capacity. No more data can be written to it, which may negatively impact the virtual machine(s). | Resize the virtual hard disk or delete unwanted files.
Vhd | IsNearlyFull | Warning | Minor | The virtual hard disk is full. | The virtual hard disk has reached its capacity. No more data can be written to it, which may negatively impact the virtual machine(s). | Resize the virtual hard disk or delete unwanted files.
Vhd | IsNearlyFull | Unhealthy | Critical | The virtual hard disk is full. | The virtual hard disk has reached its capacity. No more data can be written to it, which may negatively impact the virtual machine(s). | Resize the virtual hard disk or delete unwanted files.

## Health Fault Severity
Health Urgency | WMI Fault Severity | Perceived Severity
UNHEALTHY (2) | RED (6) | Critical Failure
WARNING (1) | YELLOW (4) | Minor Failure
HEALTHY (0) / UNKNOWN (FF) | GREEN (3) | Degraded/Warning

## Health Settings
To set these settings (PowerShell):
Get-StorageSubSystem Cluster* ¦ Set-StorageHealthSetting -Name <NAME> -Value <VALUE>
Setting Type | Settings | Data Type (unit) | Related Fault | Default | Description
Compute Fault Enable/ Disable Settings | Microsoft.Health.Setting.ComputeFaults.Enabled | Bool | ALL FAULTS BELOW | TRUE | Enables or disables all compute-related faults
Compute Fault Enable/ Disable Settings | Microsoft.Health.FaultType.Node.CPUOverloaded.Enabled | Bool | Microsoft.Health.FaultType.Node.CPUOverloaded | TRUE | Enables or disables node CPU overloaded fault
Compute Fault Enable/ Disable Settings | Microsoft.Health.FaultType.Node.VCPUToLCPU.Enabled | Bool | Microsoft.Health.FaultType.Node.VCPUToLCPU | TRUE | Enables or disables node VCPUToLCPU fault
Compute Fault Enable/ Disable Settings | Microsoft.Health.FaultType.Node.LowFreeRam.Enabled | Bool | Microsoft.Health.FaultType.Node.LowFreeRam | TRUE | Enables or disables node low free RAM fault
Compute Fault Enable/ Disable Settings | Microsoft.Health.FaultType.Node.HighRootPartitionMemoryUsage.Enabled | Bool | Microsoft.Health.FaultType.Node.HighRootPartitionMemoryUsage | TRUE | Enables or disables node high root partition memory usage fault
Compute Fault Enable/ Disable Settings | Microsoft.Health.FaultType.Node.TooHighCpuReservation.Enabled | Bool | Microsoft.Health.FaultType.Node.TooHighCpuReservation | TRUE | Enables or disables node too high CPU reservation fault
Compute Fault Enable/ Disable Settings | Microsoft.Health.FaultType.Node.TooHighMemoryUseAfterReclamation.Enabled | Bool | Microsoft.Health.FaultType.Node.TooHighMemoryUseAfterReclamation | FALSE | Enables or disables node too high memory use after reclamation fault
Compute Fault Enable/ Disable Settings | Microsoft.Health.FaultType.Node.SustainedHighCpuUsage.Enabled | Bool | Microsoft.Health.FaultType.Node.SustainedHighCpuUsage | TRUE | Enables or disables node sustained high CPU usage fault
Compute Fault Enable/ Disable Settings | Microsoft.Health.FaultType.Cluster.TooHighCpuReservation.Enabled | Bool | Microsoft.Health.FaultType.Cluster.TooHighCpuReservation | TRUE | Enables or disables cluster too high CPU reservation fault
Compute Fault Enable/ Disable Settings | Microsoft.Health.FaultType.Cluster.TooHighMemoryUseAfterReclamation.Enabled | Bool | Microsoft.Health.FaultType.Cluster.TooHighMemoryUseAfterReclamation | FALSE | Enables or disables cluster too high memory use after reclamation fault
Compute Fault Enable/ Disable Settings | Microsoft.Health.FaultType.Cluster.SustainedHighCpuUsage.Enabled | Bool | Microsoft.Health.FaultType.Cluster.SustainedHighCpuUsage | TRUE | Enables or disables cluster sustained high CPU usage fault
Compute Fault Enable/ Disable Settings | Microsoft.Health.FaultType.Vm.BadHealthState.Enabled | Bool | Microsoft.Health.FaultType.Vm.BadHealthState | TRUE | Enables or disables VM bad health state fault
Compute Fault Enable/ Disable Settings | Microsoft.Health.FaultType.Vm.BadOperationalStatus.Enabled | Bool | Microsoft.Health.FaultType.Vm.BadOperationalStatus | TRUE | Enables or disables VM bad operational status fault
Compute Fault Enable/ Disable Settings | Microsoft.Health.FaultType.Vm.GuestUnhealthy.Enabled | Bool | Microsoft.Health.FaultType.Vm.GuestUnhealthy | TRUE | Enables or disables VM guest unhealthy fault
Compute Fault Enable/ Disable Settings | Microsoft.Health.FaultType.Vm.ConfigIsOffline.Enabled | Bool | Microsoft.Health.FaultType.Vm.ConfigIsOffline | FALSE | Enables or disables VM config is offline fault
Compute Fault Enable/ Disable Settings | Microsoft.Health.FaultType.Vm.NotRespondingToControlCodes.Enabled | Bool | Microsoft.Health.FaultType.Vm.NotRespondingToControlCodes | FALSE | Enables or disables VM not responding to control codes fault
Compute Fault Enable/ Disable Settings | Microsoft.Health.FaultType.Vm.IsNearMemoryLimit.Enabled | Bool | Microsoft.Health.FaultType.Vm.IsNearMemoryLimit | TRUE | Enables or disables VM is near memory limit fault
Compute Fault Enable/ Disable Settings | Microsoft.Health.FaultType.Vhd.IsNearlyFull.Enabled | Bool | Microsoft.Health.FaultType.Vhd.IsNearlyFull | TRUE | Enables or disables VHD is nearly full fault
Compute Settings for Triggering Faults | Microsoft.Health.Setting.Node.VCPUToLCPULimit | Double | Microsoft.Health.FaultType.Node.VCPUToLCPU | 1000 | Ratio max that raises fault if value is more than virtual processor count / logical processor count
Compute Settings for Triggering Faults | Microsoft.Health.Setting.Node.AvailableToSystemMemoryLimit | Double | Microsoft.Health.FaultType.Node.LowFreeRam | 0.1 | Ratio min that raises fault if value is less than available memory (after reclamation) / total raw bytes
Compute Settings for Triggering Faults | Microsoft.Health.Setting.Node.AvailableMemoryLimit | DWORD (mb) | Microsoft.Health.FaultType.Node.LowFreeRam | 0 | Raises fault if value greater than available memory (after reclamation)
Compute Settings for Triggering Faults | Microsoft.Health.Setting.Node.MaxRootPartitionMemoryUsage | DWORD (mb) | Microsoft.Health.FaultType.Node.HighRootPartitionMemoryUsage | 0.5 | Raises fault if value * total raw bytes < root partition bytes in mb.
Compute Settings for Triggering Faults | Microsoft.Health.Setting.Cluster.MaxNodesToLose | DWORD | Microsoft.Health.FaultType.Cluster.TooHighCpuReservation | 1 | Triggers CPU reservation fault if usage exceeds threshold based on allowed node loss in the cluster.
Compute Settings for Triggering Faults | Microsoft.Health.Setting.Cluster.MaxMemoryUseAfterReclamation | Double | Microsoft.Health.FaultType.Cluster.TooHighMemoryUseAfterReclamation | 0.9 | Triggers memory fault if available memory after reclamation drops below defined threshold
Compute Settings for Triggering Faults | Microsoft.Health.Setting.Node.MaxCpuUsage | Double | Microsoft.Health.FaultType.Node.SustainedHighCpuUsage | 0.9 | Raises CPU usage fault if all recent samples exceed threshold, indicating sustained high CPU load.
Compute Settings for Triggering Faults | Microsoft.Health.Setting.VM.NearMemoryLimit | Double | Microsoft.Health.FaultType.Vm.IsNearMemoryLimit | 0.95 | Raises VM memory fault if active RAM usage exceeds threshold relative to configured RAM.
Storage Settings | System.Storage.Volume.CapacityThreshold.Enabled | Bool | Microsoft.Health.FaultType.Volume.Capacity | TRUE | When disabled, always reports volume capacity urgency as healthy; otherwise, checks thresholds.
Storage Settings | System.Storage.Volume.CapacityThreshold.Warning | Integer (%) | Microsoft.Health.FaultType.Volume.Capacity | 90 | Capacity threshold to set health urgency to warning
Storage Settings | System.Storage.Volume.CapacityThreshold.Critical | Integer (%) | Microsoft.Health.FaultType.Volume.Capacity | 95 | Capacity threshold to set health urgency to critical
Storage Settings | System.Storage.Volume.CapacityThreshold.CheckPeriodMs | Integer (ms) | Microsoft.Health.FaultType.Volume.Capacity | 300000 | Frequency in milliseconds to scan volumes for capacity thresholds
Storage Settings | System.Storage.StorageJob.CheckPeriodMs | Integer (ms) |  | 150000 | Frequency(milliseconds) at which storage jobs are queried and scanned to process relevant jobs and perform any remidiations.
Storage Settings | System.Storage.VirtualDisk.CheckPeriodMs | Integer (ms) |  | 600000 | Frequency(milliseconds) at which virtual disks are scanned for any issues.
Storage Settings | System.Storage.StoragePool.CheckPeriodMs | Integer (ms) |  | 600000 | Frequency(milliseconds) at which storage pool is scanned for various events to perform any remediations.
Storage Settings | System.Storage.StorageNode.CheckPeriodMs | Integer (ms) |  | 1800000 | Frequency(milliseconds) at which storage nodes are scanned for any issues.
Storage Settings | System.Storage.PhysicalDisk.CheckPeriodMs | Integer (ms) |  | 900000 | Frequency in milliseconds to scan physical disks for issues
Storage Settings | System.Storage.StorageScaleUnit.CheckPeriodMs | Integer (ms) |  | 1800000 | Frequency in milliseconds to scan storage scale units for issues
Storage Settings | System.Storage.StorageSubsystem.CheckPeriodMs | Integer (ms) |  | 600000 | Frequency in milliseconds to scan storage subsystem for issues
Storage Settings | System.Storage.StorageEnclosure.CheckPeriodMs | Integer (ms) |  | 600000 | Frequency in milliseconds to scan storage enclosure for issues
Storage Settings | System.Storage.PhysicalDisk.Counters.CheckPeriodMs | Integer (ms) |  | 60000 | Frequency in milliseconds to scan physical disk related counters.
Storage Settings | System.Storage.Cluster.CheckPeriodMs | Integer (ms) |  | 900000 | Frequency in milliseconds to scan cluster and cluster node events and process them.
Storage Settings | System.Storage.VirtualDisk.AutoRepair.Enabled | Bool |  | TRUE | If enabled, performs auto repair on virtual disk based on operational status and after storage pool rebalance.
Storage Settings | System.Storage.VirtualDisk.AutoRepair.DelayMs | Integer (ms) |  | 360000 | Wait time before performing the virtual disk repair after detecting that repair is needed.
Storage Settings | System.Storage.VirtualDisk.DetachedFault.Enabled | Bool | Microsoft.Health.ActionType.VirtualDisk.Detached | FALSE | If enabled, raises the alert when virtual disk is detached.
Storage Settings | System.Storage.VirtualDisk.LastCopyFault.Enabled | Bool | Microsoft.Health.ActionType.VirtualDisk.LastCopy | TRUE | If enabled, raises the alert when only last copy of the virtual disk is available in the pool.
Storage Settings | System.Storage.NewStorage.AutoRepair.Enabled | Bool |  | TRUE | If enabled, virtual disks are checked and repaired on any disk changes in the storage pool.
Storage Settings | System.Storage.NewStorage.AutoRepair.DelayMs | Integer (ms) |  | 900000 | Wait time before performing the virtual disk repair after detecting the storage changes.
Storage Settings | System.Storage.PhysicalDisk.AutoEvacuate.Enabled | Bool |  | TRUE | Determines if health should check physical disks if they need repairs
Storage Settings | System.Storage.PhysicalDisk.AutoEvacuate.DelayMs | Integer (ms) |  | 360000 | How long to delay a repair request for physical disk
Storage Settings | System.Storage.StoragePool.AutoRebalance.Enabled | Bool |  | TRUE | Determines if health should do rebalance remediation
Storage Settings | System.Storage.StoragePool.AutoRebalance.DelayMs | Integer (ms) |  | 900000 | Wait time before triggering the storage pool rebalance job. For e.g. after new disk or disk removal detection, storage pool rebalance is triggered after 15 minutes
Storage Settings | System.Storage.StoragePool.AutoPool.DelayMs | Integer (ms) |  | 60000 | Wait time before creating auto pool if autosite is enabled.
Storage Settings | System.Storage.StoragePool.AutoRebalance.PostponeIfRepairing | Bool |  | TRUE | If enabled checks for any ongoing repair for pool before rebalancing
Storage Settings | System.Storage.StoragePool.SetRetirePolicy.Enabled | Bool |  | TRUE | If enabled sets RetireMissingPhysicalDisks to Never for pool
Storage Settings | System.Storage.StoragePool.OptimizePriorityBoostOnLowSpace.Enabled | Bool |  | TRUE | If enabled on a pool, during ongoing rebalance changes IO priority to High for the pool. After rebalance completions, clears the priority for the pool.
Storage Settings | System.Storage.StoragePool.AutoRebalance.NodeStart.Enabled | Bool |  | TRUE | If enabled, reblances storage pool when a node up event is detected.
Storage Settings | System.Storage.StoragePool.AutoRebalance.PoolUnbalance.Enabled | Bool |  | TRUE | If enabled, checks for the unbalance across the disks in storage pool and triggers rebalance if unbalance is greater than the threshold configured.
Storage Settings | System.Storage.StoragePool.AutoRebalance.PoolUnbalance.IntervalMs | Integer (ms) |  | 3600000 | Time interval between checks for the storage unbalance across the disks in a pool
Storage Settings | System.Storage.StoragePool.AutoRebalance.PoolUnbalance.Threshold | Integer (percent) |  | 10 | Threshold percentage value above which rebalance is performed. If max allocated disk percentage -min allocated disk percentage is greater than 10%, rebalance is triggered.
Storage Settings | System.Storage.StoragePool.RefreshTierOnMemberChange.Enabled | Bool |  | TRUE | If enabled checks the for new drives (either SSDs SCMs HDDs) to an existing storage pool and updating the storage tier configuration to reflect the new capacity and srive types
Storage Settings | System.Storage.StoragePool.RefreshTierOnMemberChange.DelayMs | Integer (ms) |  | 60000 | Wait time before performing the storage pool tier refresh after detected the changes in disk
Storage Settings | System.Storage.StoragePool.RefreshTierOnFailure.DelayMs | Integer (ms) |  | 900000 | Wait time before performing the storage pool tier refresh after the previous tier refresh attempt failed
Storage Settings | System.Storage.StoragePool.CheckPoolReserveCapacity.Enabled | Bool | Microsoft.Health.FaultType.StoragePool.InsufficientReserveCapacity | FALSE | If enabled checks if the pool does not have enough reserve capacity and raises the alert.
Storage Settings | System.Storage.StoragePool.CheckPoolReserveCapacity.UseDiskRedundancy | Integer |  | 0 | Disk redundancy value that will be used in calculating the required reserve size for alerting. If 0, redunance is read from MSFT_ResiliencySetting
Storage Settings | System.Storage.StorageScaleUnit.SedEncKeyRotation.RetryDelaySec | Integer (s) |  | 300 | Wait time in seconds before attempting SED encryption key rotation workflow after previous attempt failed.
Storage Settings | System.Storage.StorageScaleUnit.SedEncKeyRotation.DefaultTimeoutSec | Integer (s) |  | 3600 | Timeout value in seconds for the SED encryption key rotation workflow.
Storage Settings | System.Storage.StorageScaleUnit.SedEncKey.PeriodicFaultCheck.Enabled | Bool | Microsoft.Health.FaultType.StorageScaleUnit.SedEncKey.RotationTimeout | TRUE | If enabled raises fault if SED encryption key rotation workflow on the server did not finish before timeout.
Storage Settings | System.Storage.NestedResiliency.DisableWriteCacheOnNodeDown.Enabled | Bool |  | FALSE | If enabled, automatically disables write caching when one server in a two-server cluster is down.
Storage Settings | System.Storage.NestedResiliency.DisableWriteCacheOnNodeDown.DelayMs | Integer (ms) |  | 1800000 | Wait time before disablishing write cache after one of the node is down.
Storage Settings | System.Storage.NestedResiliency.DisableWriteCacheOnNodeDown.BackoffDelayMs | Integer (ms) |  | 60000 | Wait time before attempting to disable the cache after a previous attempt to disable write cache failed.
Storage Settings | System.Storage.NestedResiliency.DisableWriteCacheOnNodeDown.ForceAllReadOnly | Bool |  | TRUE | If enabled, sets the cache in a read only mode as part of disabling the write cache in nested resiliency case.
Storage Settings | System.Storage.PhysicalDisk.AutoRetire.OnLostCommunication.Enabled | Bool | Microsoft.Health.FaultType.PhysicalDisk.LostCommunication | TRUE | Determines if health should auto-retire a disk after a lost communication fault
Storage Settings | System.Storage.PhysicalDisk.AutoRetire.OnUnresponsive.Enabled | Bool | Microsoft.Health.FaultType.PhysicalDisk.Unresponsive | TRUE | Determines if health should auto-retire a disk after it becomes unresponsive
Storage Settings | System.Storage.PhysicalDisk.AutoRetire.DelayMs | Integer (ms) |  | 900000 | How long to delay an auto-retire request for physical disk
Storage Settings | System.Storage.PhysicalDisk.AutoRetire.LastCopyDiskDelayMs | Integer (ms) |  | 86400000 | NOT USED
Storage Settings | System.Storage.PhysicalDisk.AutoRetire.SafetyThreshold | Integer (drives) |  | 2 | Prevents auto-retirement if pending disk retirements in same fault domain exceed this threshold
Storage Settings | System.Storage.PhysicalDisk.Unretire.Enabled | Bool |  | TRUE | Determines if health should attempt to unretire retired disks
Storage Settings | System.Storage.PhysicalDisk.Unretire.CountAllowed | Integer |  | 3 | Prevents unretiring a physical disk if its retry count meets or exceeds this configured limit
Storage Settings | System.Storage.PhysicalDisk.Unretire.CountResetIntervalSeconds | Integer (s) |  | 21600 | Resets a disk's unretire count if no issues occur within the configured interval
Storage Settings | System.Storage.PhysicalDisk.AutoPool.Enabled | Bool |  | FALSE | Determines if health can do physical disk auto pooling
Storage Settings | System.Storage.PhysicalDisk.AutoPool.BaseName | String |  | "AutoCreatedPool" | Used as the default name for auto-created storage pools when pooling disks in implicit or single-site configurations
Storage Settings | System.Storage.PhysicalDisk.AutoPool.SiteBaseName | String |  | "Pool for Site" | Used as the base name for auto-created pools in multi-site setups, combined with the site’s friendly name for clarity
Storage Settings | System.Storage.PhysicalDisk.AutoPool.FaultDomainAwarenessDefault | Integer (enum) |  | 3 (StorageScaleUnit) | Default fault domain awareness during pool creation. (PhysicalDisk = 1, StorageEnclosure = 2, StorageScaleUnit = 3, StorageChasis = 4, StorageRack = 5)
Storage Settings | System.Storage.PhysicalDisk.AutoPool.DelayMs | Integer (ms) |  | 60000 | How long to delay an auto-pool request for physical disks
Storage Settings | System.Storage.PhysicalDisk.S2DCacheCheck.Enabled | Bool |  | TRUE | Determines if many checks on physical disks should occur. This includes operations on disk cache records, disk retiring, and several fault checks
Storage Settings | System.Storage.PhysicalDisk.QuarantineEnforce.Enabled | Bool |  | TRUE | Triggers validation and processing of quarantine-related disk configuration or firmware updates
Storage Settings | System.Storage.PhysicalDisk.QuarantineReport.Enabled | Bool |  | TRUE | Enables logging or fault creation based on disk compliance status without enforcing quarantine actions
Storage Settings | System.Storage.PhysicalDisk.QuarantineInHealth.Enabled | Bool |  | FALSE | Allows the system to adjust S2D disk usage based on quarantine status within the Health subsystem
Storage Settings | System.Storage.PhysicalDisk.QuarantineInSbl.Enabled | Bool |  | TRUE | Enables quarantine handling logic within the SBL (Storage Bus Layer), triggering config or firmware update notifications
Storage Settings | System.Storage.PhysicalDisk.AutoFirmwareUpdate.DelayMs | Integer (ms) |  | 60000 | Sets the minimum wait time before starting a firmware update, ensuring controlled rollout scheduling and pacing
Storage Settings | System.Storage.PhysicalDisk.AutoFirmwareUpdate.AlwaysApply | Bool |  | FALSE | NOT USED
Storage Settings | System.Storage.PhysicalDisk.AutoFirmwareUpdate.SingleDrive.Enabled | Bool |  | TRUE | Allows firmware updates to be applied individually to disks, enabling targeted remediation instead of full-scale rollouts
Storage Settings | System.Storage.PhysicalDisk.AutoFirmwareUpdate.RollOut.Enabled | Bool |  | TRUE | Controls whether firmware updates are deployed across multiple disks as a coordinated rollout rather than individually
Storage Settings | System.Storage.PhysicalDisk.AutoFirmwareUpdate.RollOut.LongDelaySeconds | Integer (s) |  | 604800 (7 days) | Specifies the wait time (in seconds) before the next firmware rollout when a fault domain has had fewer updates, requiring a longer stabilization period
Storage Settings | System.Storage.PhysicalDisk.AutoFirmwareUpdate.RollOut.ShortDelaySeconds | Integer (s) |  | 86400 (1 day) | Defines the shorter wait time (in seconds) between firmware rollouts when recent updates were sufficient and no extended delay is needed
Storage Settings | System.Storage.PhysicalDisk.AutoFirmwareUpdate.RollOut.LongDelayCount | Integer (%) |  | 1 | Determines how many times a firmware can be updated in a fault domain before requiring a longer delay
Storage Settings | System.Storage.PhysicalDisk.AutoFirmwareUpdate.RollOut.FailureTolerance | Integer |  | 3 | Sets the maximum number of allowed failed firmware updates before halting the rollout process to prevent further issues
Storage Settings | System.Storage.PhysicalDisk.AutoFirmwareUpdate.RollOut.FaultDomainRetryDelayMs | Integer (ms) |  | 1800000 | Defines how long to wait before retrying firmware updates in fault domains that previously failed due to maintenance mode issues
Storage Settings | System.Storage.PhysicalDisk.AutoReplace.Enabled | Bool |  | TRUE | Allows automatic detection and replacement of failed or missing disks based on location and operational status
Storage Settings | System.Storage.PhysicalDisk.AutoReplace.IgnoreS2DVirtualEnclosure.Enabled | Bool |  | TRUE | Controls whether disks in S2D enclosures are excluded from auto-replacement checks due to unreliable slot-to-location mapping
Storage Settings | System.Storage.PhysicalDisk.AutoReplace.SupportNVMe.Enabled | Bool |  | TRUE | Controls whether NVMe drives are included in automatic disk replacement checks. If disabled, NVMe disks are skipped
Storage Settings | System.Storage.PhysicalDisk.Unresponsive.Fault.Enabled | bool | Microsoft.Health.FaultType.PhysicalDisk.Unresponsive | TRUE | Controls whether a fault is raised when a disk becomes unresponsive and exceeds configured thresholds
Storage Settings | System.Storage.PhysicalDisk.Unresponsive.Fault.Threshold | Integer | Microsoft.Health.FaultType.PhysicalDisk.Unresponsive | 3 | Number of restores before an alert is raised
Storage Settings | System.Storage.PhysicalDisk.Unresponsive.Reset.Enabled | bool |  | TRUE | Controls whether unresponsive disks are eligible for automatic recovery instead of immediately triggering faults or retirement
Storage Settings | System.Storage.PhysicalDisk.Unresponsive.Reset.DelaySeconds | Integer (s) |  | 300 | Defines the minimum time a disk must remain in an unresponsive state before it is eligible for a restore attempt
Storage Settings | System.Storage.PhysicalDisk.Unresponsive.Reset.CountAllowed | Integer |  | 3 | Sets the maximum number of times a disk can be automatically restored from an unresponsive state before triggering a fault or retirement
Storage Settings | System.Storage.PhysicalDisk.Unresponsive.Reset.CountResetIntervalSeconds | Integer (s) |  | 3600 | Defines the time (in seconds) a disk must remain responsive before its unresponsive reset count is cleared, allowing future recovery attempts
Storage Settings | System.Storage.PhysicalDisk.S2D.Unresponsive.Fault.Enabled | bool | Microsoft.Health.FaultType.PhysicalDisk.SblUnresponsive | TRUE | Activates tracking of disk timeout failures (write/read) to determine unresponsiveness based on count thresholds
Storage Settings | System.Storage.PhysicalDisk.S2D.Unresponsive.Count.IncludeReadTimeouts | bool | Microsoft.Health.FaultType.PhysicalDisk.SblUnresponsive | TRUE | Determines whether read timeout failures are included alongside write timeouts when evaluating disk unresponsiveness
Storage Settings | System.Storage.PhysicalDisk.S2D.Unresponsive.Count.Threshold | Integer | Microsoft.Health.FaultType.PhysicalDisk.SblUnresponsive | 0 | Sets the maximum allowed combined read/write timeout failures before a disk is considered unresponsive by SBL logic
Storage Settings | System.Storage.PhysicalDisk.S2D.MediaFailure.Enabled | Bool | Microsoft.Health.FaultType.PhysicalDisk.SblMediaFailed | TRUE | Activates tracking of media failure counts to determine if a disk should be faulted or drained
Storage Settings | System.Storage.PhysicalDisk.S2D.MediaFailure.Write.Threshold | Integer | Microsoft.Health.FaultType.PhysicalDisk.SblMediaFailed | 5 | Sets the maximum number of write media failures allowed before a disk is flagged as degraded or failing
Storage Settings | System.Storage.PhysicalDisk.S2D.MediaFailure.Read.Threshold | Integer | Microsoft.Health.FaultType.PhysicalDisk.SblMediaFailed | 5 | Sets the maximum number of read media failures allowed before a disk is considered degraded or failing
Storage Settings | System.Storage.PhysicalDisk.S2D.MediaFailure.NeverRebindWhenDirty | Bool |  | FALSE | Prevents rebind of cache disks if any dirty data exists, regardless of last-copy status
Storage Settings | System.Storage.PhysicalDisk.S2D.MediaFailure.UseDrainRemediation | Bool |  | TRUE | Enables draining and recovery workflows for cache disks with media failures instead of immediately marking them as failed
Storage Settings | System.Storage.PhysicalDisk.S2D.MediaFailure.Drain.TimeoutSeconds | Integer (s) |  | 900 | Sets the maximum time allowed for draining dirty data from a failed cache disk before triggering repair actions
Storage Settings | System.Storage.PhysicalDisk.S2D.MediaFailure.Drain.CheckPeriodMs | Integer (ms) |  | 60000 | Sets how often (in milliseconds) to check drain progress before retrying or triggering repair actions
Storage Settings | System.Storage.PhysicalDisk.S2D.MediaFailure.Drain.AutoRecover | Bool |  | TRUE | Enables automatic recovery of a cache disk after a successful drain, avoiding manual intervention or permanent faulting
Storage Settings | System.Storage.PhysicalDisk.MaintenanceModeCommand.Enabled | Bool |  | TRUE | Controls whether maintenance mode commands can be processed, enabling workflows like disk isolation or repair actions
Storage Settings | System.Storage.PhysicalDisk.MaintenanceModeCommand.OnSuspend.Enabled | Bool |  | TRUE | Enables maintenance mode when a disk is suspended.
Storage Settings | System.Storage.PhysicalDisk.MaintenanceModeCommand.TimeoutSeconds | Integer (s) |  | INT_MAX - 1 | Sets timeout duration for maintenance mode operations in seconds
Storage Settings | System.Storage.PhysicalDisk.MaintenanceModeCommand.Drain.TimeoutSeconds | Integer (s) |  | 900 | Maximum time allowed to drain disk before maintenance begins
Storage Settings | System.Storage.PhysicalDisk.MaintenanceModeCommand.Drain.CheckPeriodMs | Integer (ms) |  | 10000 | Interval in milliseconds to check disk drain progress
Storage Settings | System.Storage.PhysicalDisk.MaintenanceModeCommand.NonPoolIntent.Enabled | Bool |  | FALSE | Allows maintenance mode for disks not in a storage pool
Storage Settings | System.Storage.PhysicalDisk.MaintenanceModeCommand.SystemInitiated.NonSsuAllowed | Bool |  | FALSE | Permits system-initiated maintenance on non-SSU entities
Storage Settings | System.Storage.PhysicalDisk.MaintenanceModeCommand.Callback.TimeoutMs | Integer (ms) |  | 300000 | Timeout for maintenance mode callback operations in milliseconds
TSDB Settings | System.PerformanceHistory.Path | String |  | "" | Filesystem location where the performance history database (TSDB) is stored
TSDB Settings | System.PerformanceHistory.AutoProvision.Enabled | Bool |  | FALSE | Automatically provisions TSDB volumes if not already present during setup or validation
TSDB Settings | System.PerformanceHistory.Volume.SizeMB | Integer (mb) |  | 20480 | Specifies the size in megabytes for the main TSDB data volume
TSDB Settings | System.PerformanceHistory.SR.Log.Volume.SizeMB | Integer (mb) |  | 20480 | Defines the size in megabytes for the Storage Replica log volume used by TSDB
TSDB Settings | System.PerformanceHistory.DeleteHistory | Bool |  | FALSE | Enables deletion of existing TSDB performance history data during reconfiguration or cleanup
TSDB Settings | System.PerformanceHistory.StretchSR.Enabled | Bool |  | TRUE | Enables multi-site Storage Replica support for performance history
TSDB Settings | System.PerformanceHistory.Gc.Start | String |  | "1:00" | Time of day (HH:MM) when garbage collection starts
TSDB Settings | System.PerformanceHistory.Gc.Period | Integer (hr) |  | 24 | Frequency in hours for running garbage collection
TSDB Settings | System.PerformanceHistory.Gc.LastConsideredStream | String |  | "LastWeek" | Tracks the last data stream considered during garbage collection
TSDB Settings | System.PerformanceHistory.MaxCachePages | Integer |  | 51200 | Maximum number of cache pages used by performance history
TSDB Settings | System.PerformanceHistory.MaxOutstandingIOs | Integer |  | 300 | Limits the number of concurrent I/O operations
TSDB Settings | System.PerformanceHistory.MaxOngoingMessages | Integer |  | 50 | Maximum number of in-flight messages being processed
TSDB Settings | System.PerformanceHistory.MaxQueuedMessages | Integer |  | 100 | Maximum number of messages allowed in the queue
TSDB Settings | System.PerformanceHistory.Batch.Min.Messages | Integer |  | 10 | Minimum number of messages to trigger a batch write
TSDB Settings | System.PerformanceHistory.Batch.Max.Interval | Integer (ms) |  | 1000 | Maximum wait time (ms) before flushing a batch
TSDB Settings | System.PerformanceHistory.Jet.Param.MaxVerPages | Integer |  | 8192 | Maximum version pages allowed by the Jet database engine
TSDB Settings | System.PerformanceHistory.Jet.Param.MaxOpenTables | Integer |  | 10000 | Maximum number of open tables allowed in Jet database
TSDB Settings | System.PerformanceHistory.Jet.Param.MaxTermporaryTables | Integer |  | 10000 | Maximum number of temporary tables allowed in Jet database
Other Settings | System.LogLevel | Integer (enum) |  | 0 | Level of logs to produce (1 - Error, 2 - Warning, 3 - Info, 4 - Noise, Other - Debug)
Other Settings | System.StaleFaultThreshold.Second | Integer (s) |  | 259200 (3 days) | Time to hold stale (not recently reported) health alerts/faults. Setting only applied during leader activation.

## Collected Metrics
Metrics Type | Metrics
Compute VM | Microsoft.Health.Metric.VM.MemoryConsumed
Compute VM | Microsoft.Health.Metric.VM.MemoryMaxAllowed
Compute VM | Microsoft.Health.Metric.VM.MemoryOSUsed
Compute VM | Microsoft.Health.Metric.VM.CPUReservation
Compute VM | Microsoft.Health.Metric.VM.CPUUtilization
Compute VM | Microsoft.Health.Metric.VM.HealthState
Compute VM | Microsoft.Health.Metric.VM.OperationalStatus
Compute VM | Microsoft.Health.Metric.VM.GuestState
Compute Cluster | Microsoft.Health.Metric.Cluster.VCPU
Compute Cluster | Microsoft.Health.Metric.Cluster.LCPU
Compute Cluster | Microsoft.Health.Metric.Cluster.VCPUToLCPU
Compute Cluster | Microsoft.Health.Metric.Cluster.TotalCPUPercentage
Compute Cluster | Microsoft.Health.Metric.Cluster.RootCPUUsage
Compute Cluster | Microsoft.Health.Metric.Cluster.TotalCPUUsage
Compute Cluster | Microsoft.Health.Metric.Cluster.VMCPUUsage
Compute Cluster | Microsoft.Health.Metric.Cluster.SystemMemory
Compute Cluster | Microsoft.Health.Metric.Cluster.RootMemory
Compute Cluster | Microsoft.Health.Metric.Cluster.HyperVAvailableMemory
Compute Cluster | Microsoft.Health.Metric.Cluster.HyperVAvailableMemoryAfterReclamation
Compute Cluster | Microsoft.Health.Metric.Cluster.CPUSReserved
Compute Node | Microsoft.Health.Metric.Node.VHDmaximumTotal
Compute Node | Microsoft.Health.Metric.Node.VHDUsedTotal
Compute Node | Microsoft.Health.Metric.Node.GuestMemoryTotal
Compute Node | Microsoft.Health.Metric.Node.GuestMemoryMaximum
Compute Node | Microsoft.Health.Metric.Node.VCPU
Compute Node | Microsoft.Health.Metric.Node.LCPU
Compute Node | Microsoft.Health.Metric.Node.VCPUToLCPU
Compute Node | Microsoft.Health.Metric.Node.SystemMemory
Compute Node | Microsoft.Health.Metric.Node.RootMemory
Compute Node | Microsoft.Health.Metric.Node.HyperVAvailableMemory
Compute Node | Microsoft.Health.Metric.Node.HyperVAvailableMemoryAfterReclamation
Compute Node | Microsoft.Health.Metric.Node.TotalCPUPercentage
Compute Node | Microsoft.Health.Metric.Node.TotalCPUUsage
Compute Node | Microsoft.Health.Metric.Node.TotalHostCPUUsage
Compute Node | Microsoft.Health.Metric.Node.RootCPUUsage
Compute Node | Microsoft.Health.Metric.Node.VMCPUUsage
Compute Node | Microsoft.Health.Metric.Node.VMCPUSReserved
TSDB Physical Disk | physicaldisk.iops.read
TSDB Physical Disk | physicaldisk.iops.write
TSDB Physical Disk | physicaldisk.iops.total
TSDB Physical Disk | physicaldisk.latency.read
TSDB Physical Disk | physicaldisk.latency.write
TSDB Physical Disk | physicaldisk.latency.average
TSDB Physical Disk | physicaldisk.throughput.read
TSDB Physical Disk | physicaldisk.throughput.write
TSDB Physical Disk | physicaldisk.throughput.total
TSDB Physical Disk | physicaldisk.capacity.size.used
TSDB Physical Disk | physicaldisk.capacity.size.total
TSDB Physical Disk | Physicaldisk.Cache.Size.Total
TSDB Physical Disk | Physicaldisk.Cache.Size.Dirty
TSDB Physical Disk | physicaldisk.alltime.endurance.RecordingStarted
TSDB Physical Disk | physicaldisk.alltime.endurance.RecordedTime
TSDB Physical Disk | physicaldisk.alltime.endurance.TBW
TSDB Physical Disk | physicaldisk.alltime.endurance.DWPD
TSDB Physical Disk | physicaldisk.periodic.IO.Total
TSDB Physical Disk | physicaldisk.periodic.IO.Failed
TSDB Physical Disk | physicaldisk.periodic.latency.average
TSDB Physical Disk | physicaldisk.periodic.latency.maximum
TSDB Physical Disk | physicaldisk.periodic.latency.bucket.128us
TSDB Physical Disk | physicaldisk.periodic.latency.bucket.256us
TSDB Physical Disk | physicaldisk.periodic.latency.bucket.512us
TSDB Physical Disk | physicaldisk.periodic.latency.bucket.1ms
TSDB Physical Disk | physicaldisk.periodic.latency.bucket.4ms
TSDB Physical Disk | physicaldisk.periodic.latency.bucket.16ms
TSDB Physical Disk | physicaldisk.periodic.latency.bucket.64ms
TSDB Physical Disk | physicaldisk.periodic.latency.bucket.128ms
TSDB Physical Disk | physicaldisk.periodic.latency.bucket.256ms
TSDB Physical Disk | physicaldisk.periodic.latency.bucket.512ms
TSDB Physical Disk | physicaldisk.periodic.latency.bucket.1s
TSDB Physical Disk | physicaldisk.periodic.latency.bucket.2s
TSDB Physical Disk | physicaldisk.periodic.latency.bucket.6s
TSDB Physical Disk | physicaldisk.periodic.latency.bucket.10s
TSDB Physical Disk | physicaldisk.periodic.latency.bucket.20s
TSDB Physical Disk | physicaldisk.periodic.latency.bucket.30s
TSDB Physical Disk | physicaldisk.periodic.latency.bucket.10s.Plus
TSDB Cluster Node | clusternode.cpu.usage
TSDB Cluster Node | clusternode.cpu.usage.guest
TSDB Cluster Node | clusternode.cpu.usage.host
TSDB Cluster Node | clusternode.memory.total
TSDB Cluster Node | clusternode.memory.available
TSDB Cluster Node | clusternode.memory.usage.guest
TSDB Cluster Node | clusternode.memory.usage.host
TSDB Cluster Node | clusternode.memory.usage
TSDB Cluster Node | clusternode.CsvCache.Iops.Read.Hit
TSDB Cluster Node | clusternode.CsvCache.Iops.Read.Miss
TSDB Cluster Node | clusternode.CsvCache.Iops.Read.HitRate
TSDB Cluster Node | clusternode.SblCache.Iops.Read.Hit
TSDB Cluster Node | clusternode.SblCache.Iops.Read.Miss
TSDB Cluster Node | clusternode.SblCache.Iops.Read.HitRate
TSDB Cluster Node | clusternode.Storage.Used
TSDB Cluster Node | clusternode.Storage.Degraded
TSDB Virtual Machine | vm.cpu.usage
TSDB Virtual Machine | vm.memory.total
TSDB Virtual Machine | vm.memory.available
TSDB Virtual Machine | vm.memory.assigned
TSDB Virtual Machine | vm.memory.pressure
TSDB Virtual Machine | vm.memory.minimum
TSDB Virtual Machine | vm.memory.maximum
TSDB Virtual Machine | vm.memory.startup
TSDB Virtual Hard Disk | vhd.latency.average
TSDB Virtual Hard Disk | vhd.throughput.read
TSDB Virtual Hard Disk | vhd.iops.read
TSDB Virtual Hard Disk | vhd.throughput.write
TSDB Virtual Hard Disk | vhd.iops.write
TSDB Virtual Hard Disk | vhd.iops.total
TSDB Virtual Hard Disk | vhd.throughput.total
TSDB Virtual Hard Disk | vhd.size.current
TSDB Virtual Hard Disk | vhd.size.maximum
TSDB VM Network Adapter | vmnetworkadapter.bandwidth.inbound
TSDB VM Network Adapter | vmnetworkadapter.bandwidth.outbound
TSDB VM Network Adapter | vmnetworkadapter.bandwidth.total
TSDB Volume | volume.iops.read
TSDB Volume | volume.iops.write
TSDB Volume | volume.iops.total
TSDB Volume | volume.latency.read
TSDB Volume | volume.latency.write
TSDB Volume | volume.latency.average
TSDB Volume | volume.throughput.read
TSDB Volume | volume.throughput.write
TSDB Volume | volume.throughput.total
TSDB Volume | volume.size.available
TSDB Volume | volume.size.total
TSDB Net Adapter | netadapter.bandwidth.inbound
TSDB Net Adapter | netadapter.bandwidth.outbound
TSDB Net Adapter | netadapter.bandwidth.total
TSDB Net Adapter | netadapter.bandwidth.rdma.inbound
TSDB Net Adapter | netadapter.bandwidth.rdma.outbound
TSDB Net Adapter | netadapter.bandwidth.rdma.total